## Slide 1
© Yottacontrol 2012
Yottacontrol A Series Distributed Control System
A-118X
1. Hardware Vision
2. Overview and Facility
For further information, please visit : www.yottacontrol.com
3. Accessories
A-118x User Quick Manual
Item | Description
1 | Inputs
2 | Memory Card Slot
3 | Indicator, Red: initial mode, Green: normal (run) mode, Spark: no program in controller
4 | Inputs
5 | Communication Port
6 | Incoming Power
7 | Buttons
8 | LCD display
9 | Outputs
Overview | Facility | 
Function Block Diagram + Ladder Diagram system | Function Blocks | 1024
Redundant function | Digital Inputs | 256
Support Start-up Screen (108*64 ) | Digital Outputs | 128
Multiple communication port | Flag | 512
Password protection, copy protection | Analog Inputs | 64
36 integrated functions, pre-tested functions | Text Box | 16
Linking of 1024 function block is possible | Analog outputs | 32
Display of message texts | Block names | 256
Integrated data latch | Analog flags | 512
Flexibly expandable up to 10000 points | Shift register | 1
Support full Modbus protocol | Shift register bits | 16
Free PC software“Yotta Edit”+“Yotta Utility” | Open connectors | 128
Available adjust program parameter on the controller without a PC. | Timer/Counter | 1024 / 1024
ATP | DSCAB | AMB64 | Remote Modules
P1
V1.00

## Slide 2
© Yottacontrol 2012
Yottacontrol A Series Distributed Control System
A-118X
4. Technical Specifications
For further information, please visit : www.yottacontrol.com
A-118x User Quick Manual
Type | A-1188S | A-1188 | A-1188D | A-1189S | A-1189 | A-1189D
 | A-1188S-T | A-1188-T | A-1188D-T | A-1189S-T | A-1189-T | A-1189D-T
Digital Inputs | 8 |  |  | 8 |  | 
Analog Inputs | -- |  |  | 4 (able to use in digital specification) |  | 
Digital Outputs | 4 |  |  | 4 |  | 
Input voltage range | Digital ON: 4~30VDC OFF:2VDC(max) |  |  | Digital ON: 4~30VDC OFF:2VDC(max) |  | 
 |  |  |  | Analog: 0~10VDC |  | 
Continuous Current | Relay: 5 A for resistive load, 2 A for inductive load Transistor: NPN open collector, max. 100mA at 30 VDC |  |  |  |  | 
Incoming Power | 10~30 VDC |  |  |  |  | 
Integrated time switches/reserve power | Yes / > 2 years |  |  |  |  | 
Operation temperature | -20°C to +75 °C |  |  |  |  | 
Storage temperature | -25 °C to +80 °C |  |  |  |  | 
Linking of functions | 1024(Max) |  |  |  |  | 
Real time clock | Yes |  |  |  |  | 
Protocols | Modbus RTU/Modbus ASCII |  |  |  |  | 
Incorporate operator interface | Yes- with Modbus interface |  |  |  |  | 
Expansion maximum I/O | More than 10000 |  |  |  |  | 
Input Operating frequency | 15000HZ(DI0~DI3) |  |  |  |  | 
Message text/ display | 4 lines of 12 characters |  |  |  |  | 
Communication Port | RS232*1 | RS485*2 +RS232*1 | RS485*2 +RS232*1 | RS232*1 | RS485*2 +RS232*1 | RS485*2 +RS232*1
Type Instruction | A-118XS: Without LED indicator and LCD monitor, Relay output A-118XS-T：Without LED indicator and LCD monitor, Transistor output A-118X: LED indicator, Relay output A-118X-T：LED indicator, Transistor output A-118XD：LCD monitor, Relay output A-118XD-T：LCD monitor, Transistor output |  |  |  |  | 
P2
V1.00

## Slide 3
© Yottacontrol 2012
Yottacontrol A Series Distributed Control System
A-118X
5. Communicate with PC via Yottacontrol Converter or DSCAB
For further information, please visit : www.yottacontrol.com
A-118x User Quick Manual
Step1. Prepare controller and Converter or DSCAB | Step2. Turn the controller’s status to ‘init
Step3. Link controller to converter via twisted pair cable | Step4. Or linked DSCAB
Step5. Turn on the controller’s power | Step6. Click Yottacontrol Utility and search the device
P3
V1.00

## Slide 4
© Yottacontrol 2012
Yottacontrol A Series Distributed Control System
A-118X
5. Communicate with PC via Yottacontrol Converter or DSCAB
For further information, please visit : www.yottacontrol.com
A-118x User Quick Manual
Step7. Searching is finished | Step8. Click YottaEditor to confirm controller’s com port
Step9. Now you can compile program via YottaEditor | 
6. Display menu structure and application wiring
P4
V1.00

## Slide 5
© Yottacontrol 2012
Yottacontrol A Series Distributed Control System
A-118X
7. YottaEditor
For further information, please visit : www.yottacontrol.com
A-118x User Quick Manual
Item | Description | 
1 | Menu bar | 
2 | Standard toolbar | 
3 | Programming interface | 
4 | Information window | 
5 | Status bar | 
6 | Constants and connectors Basic functions Special functions | 
Main screen
In this tab, you can enter detailed information of a circuit program.
Properties-General
P5
V1.00

## Slide 6
© Yottacontrol 2012
Yottacontrol A Series Distributed Control System
A-118X
7. YottaEditor
For further information, please visit : www.yottacontrol.com
A-118x User Quick Manual
All parameters are transferred between PC and controller, and then saved there after the circuit program is downloaded.
Properties-Parameter
Program Name
A program name with up to 16 characters can be entered for the circuit program.
Program Password
A program password with up to 8 alphabetical characters can be assigned to protect the circuit program on controller. Enter 2 identical passwords in New Password and Repeat New Password text boxes separately to assign a new password for your circuit program. You can delete the assigned password by leaving New Password and Repeat New Password text boxes empty.
You can open or edit the circuit program from YottaEditor at any time no matter if the program is password-protected or not. For password-protected circuit programs, you have to enter the password to view or modify the program on controller, or to load the circuit program from controller to YottaEditor.
Redundancy
Controller provides redundancy to help you build a robust system. In case the server is going down there is a backup server that can take over the job.
There are 3 types for you to choose.
None: Redundancy is not available for this type.
Master: Connected controller is the main controller of the whole system. It communicates with Slave continuously.
Slave: Connected controller becomes Master automatically, if it doesn't receive signals from the Master after a period of time which is defined in the Synchronizing time text box in millisecond.
P6
V1.00

## Slide 7
© Yottacontrol 2012
Yottacontrol A Series Distributed Control System
A-118X
7. YottaEditor
For further information, please visit : www.yottacontrol.com
A-118x User Quick Manual
Copy Protect When select this function, can protect program illegal download without the correct password. Temperature Protect point Set the temperature range. If work temperature surpasses the range, memory will record.
Properties-Protect
P7
V1.00

## Slide 8
© Yottacontrol 2012
Yottacontrol A Series Distributed Control System
A-118X
7. YottaEditor
For further information, please visit : www.yottacontrol.com
A-118x User Quick Manual
You can set the following parameters. Model: Master, Slave, ATP (A series text panel) Device address: From 1 to 255 (for slave only) Protocol: Modbus-RTU, Modbus-ASCII Baud rate: 1200, 2400, 4800, 9600, 14.4K, 19.2K, 28.8K, 38.4K, 57.6K, 115.2K, 230.4K (bps) Parity/Data bit/ Stop bit: None, 8, 1/None, 8, 2/Odd, 8, 1/Odd, 8, 2/Even, 8, 1/Even , 8, 2 Timeout: In millisecond Delay between polls: In millisecond Data register index: High Low, Low High
Properties-COM
P8
V1.00

## Slide 9
© Yottacontrol 2012
Yottacontrol A Series Distributed Control System
A-118X
7. YottaEditor
For further information, please visit : www.yottacontrol.com
A-118x User Quick Manual
You can place any image into the controller in *.bmp format (108*64)
The device selection dialog shows you which blocks and memory resources are available to you. If you have already created a circuit program or are using some blocks, the hardware selection dialog offers you only the A/B-Series devices you can operate with the currently used blocks.
Properties-Startup Bmp
Properties-Hardware
P9
V1.00

## Slide 10
© Yottacontrol 2012
Yottacontrol A Series Distributed Control System
A-118X
7. YottaEditor
For further information, please visit : www.yottacontrol.com
A-118x User Quick Manual
Choose a COM port from the list, if you know exactly which one connects to the controller. If you are not sure which COM port connects to the controller, you can let YottaEditor automatically detect the COM port.
This command can be used to read and set the date and time of connected controller. Click on the Current Time button to apply the system time of PC in YottaEditor.
Options-Communication Configuration
Tools-Transfer-Clock Setting/Calibration
P10
V1.00

## Slide 11
© Yottacontrol 2012
Yottacontrol A Series Distributed Control System
A-118X
7. YottaEditor
For further information, please visit : www.yottacontrol.com
A-118x User Quick Manual
This menu command lets you set an automatic conversion of the summer and winter time for the controller’s clock.
Tools-Transfer-SummerTime/WinterTime
When you enable summer/winter time conversion, you can specify a country-specific time conversion:
*EU: European Union
*UK: United Kingdom of Great Britain and Northern Ireland
*US: United States of America
*Australia
*Tasmania
*New Zealand
*Freely adjustable: customized switchover dates and times
For the "Freely adjustable" selection, you specify the month and day of the switchover. The start time of summer time is 02:00 + the entered time difference; the end time is 03:00 – the entered time difference.
Note: The United States of America redefined the daylight saving time (summer time) / standard time (winter time) switchover dates in 2007. Controller, however, uses the switchover dates as they were prior to 2007. To use the new U.S. switchover times, you must configure a “Freely adjustable” setting that corresponds to the new rule where Daylight Saving Time is in effect from 2:00 a.m. on the second Sunday in March until 2:00 a.m. on the first Sunday in November according to the local time zone.
P11
V1.00

## Slide 12
© Yottacontrol 2012
Yottacontrol A Series Distributed Control System
A-118X
7. YottaEditor
For further information, please visit : www.yottacontrol.com
A-118x User Quick Manual
Simulation Click on the Tools -> Simulation menu command or the simulation icon in the standard toolbar to start simulation.
Simulation Toolbar The simulation toolbar, which is shown as follows, is active when the program is in simulation mode. Use this tool to perform the simulation
Simulation Control Icons
Time Control For a time-sensitive circuit program, you can use the time control to observe the processes of the circuit program. This is a simple but effective way to predict the result of the program operation.
Status Display The value of signal and corresponding connecting line is as follows:
 | Simulate a power failure.
 | Start simulation.
 | Stop simulation
 | Suspend simulation. The Circuit program switches into suspend mode. Resume simulation
 | Start/stop the simulation in stepping mode. It's available in suspend mode.
 | Set a specific period of time or set a specific number of cycles. Depends on the below control.
 | Choose one of the four modes: cycle, second, minute and hour.
 | Display the current time in YottaEditor.
 | Modify the current time in YottaEditor.
The value of signal | The color of corresponding connecting line | 
1 | Red | 
0 | Blue | 
P12
V1.00

## Slide 13
© Yottacontrol 2012
Yottacontrol A Series Distributed Control System
A-118X
7. YottaEditor
For further information, please visit : www.yottacontrol.com
A-118x User Quick Manual
Connect ATP to Controller and select the COM model to ATP.
Now available adjust program parameter in the ATP without a PC. And controller will show ‘ATP Connect’.
Yottacontrol A Series Text Panel (ATP)
P13
V1.00

## Slide 14
© Yottacontrol 2012
Yottacontrol A Series Distributed Control System
A-118X
8. YottaUtility
For further information, please visit : www.yottacontrol.com
A-118x User Quick Manual
Main screen
When the controller is in initial mode, you can see the following figure.
Initial mode
P14
V1.00

## Slide 15
© Yottacontrol 2012
Yottacontrol A Series Distributed Control System
A-118X
8. YottaUtility
For further information, please visit : www.yottacontrol.com
A-118x User Quick Manual
The general settings are read only. | The function of each button is as follows
Calibration and Weekday are read only. | 
You can set Year, Month, Day and Time. Press the Update button to store the changed values. Press the Restore button to restore the RTC value from the controller's memory. The Update and Restore buttons are available when the Weekday or Time values are changed. Press the Sync button to synchronize the RTC time with PC. | 
General setting
 | You can find more information about the controller.
 | The database window shows up.
P15
V1.00

## Slide 16
© Yottacontrol 2012
Yottacontrol A Series Distributed Control System
A-118X
8. YottaUtility
For further information, please visit : www.yottacontrol.com
A-118x User Quick Manual
When the button is pressed, you can see the following figure
This page provides the detailed information of digital signals, such as inputs, outputs, flags and shift registers
This page lets you get a deep view of the information and status of the controller. The data read from the controller provide the information and status. The label on the left side of each data indicates the meaning of each data.
Controller Information-System Info
Controller Information-Digital
P16
V1.00

## Slide 17
© Yottacontrol 2012
Yottacontrol A Series Distributed Control System
A-118X
8. YottaUtility
For further information, please visit : www.yottacontrol.com
A-118x User Quick Manual
This page provides the detailed information of analog signals, such as inputs, outputs and flags
This page provides the detailed information of function block. Please refer YottaUtility following table
Controller Information-Analog
Controller Information-Function Block
P17
V1.00

## Slide 18
© Yottacontrol 2012
Yottacontrol A Series Distributed Control System
A-118X
8. YottaUtility
For further information, please visit : www.yottacontrol.com
A-118x User Quick Manual
When the button is pressed, you can see the following figure
Database Contents
We provide users with database functions. Users can store the values of selected modules into the database. These data can be retrieved from the database for further analysis in the future.
Note: The database is a Microsoft Access file. The file name is app_path\ARController.mdb.
Note: The file backups automatically when its size exceeds 500 MB. The backup file name is ARControllerYYYYMMDD.mdb.
Note: The file app_path\ARControllerTemplate.mdb should not be modified and deleted.
The below instructions show you how to manipulate the database.
Stop inserting data into the database.
Inserting data into the database.
Specify the time interval for inserting data into the database.
How to Use the Database
In the previous figure, users can retrieve and delete data from the database. The combination of all drop-down boxes is the criteria for retrieving and deleting data.
Note: The star sign (*) in drop-down boxes means all.
Note: If the number of retrieving data is more than 3000. You have to reset the selection criteria.
The below instructions show you more information about data manipulation.
Retrieve data from the database.
Delete data from the database.
Export data to Excel.
Close the form.
P18
V1.00